## Log Inactivation Overview
Step 2 Determine Effective Volume
The effective volume of the disinfection segment refers to the volume of a basin or pipeline that is available to provide adequate contact time for the disinfectant.
Effective volumes are calculated based on worst case operating conditions using the minimum operating depths, in the case of basins.
This is especially critical in plants where high service pumps significantly change the operating levels of the clearwell and in plants that use backwash systems supplied from the clearwell.
Rectangular Basin (l x w x d)
Length (l) = 50 (ft)
Width (w) = 40 (ft)
Dept of water (d) = 11 (ft)
Volume (V) = 50 ft x 40 ft x 11ft
= 22,000 ft^3
Multiply the volume in ft3 on lime 4 by 7.48 gal/ft^3 to get effective volume in gallons.
V = 22,000 ft^3 x 7.48 gal/ft^3 = 164,560 gallons
Cylinder Basin (pi x r^2 x d)
pi = 3.14
Radius (r) = 40 ft
Depth of Basin (Low Water Mark) = 20 ft
V = 3.14 x 40 ft^2 x 20 ft = 100,480 ft^3
V = 100,480 ft^3 x 7.48 gal/ft^3 = 751,590 gal
Pipeline
Volume per Foot of Pipe = .0408 x D^2 (D in Inches)
D = 6 Inches
Volume per Foot of Pipe = 0.0408 x (6)^2
= 1.4688 gal per foot
L = 1 mile = 5280 feet
V = 7755 gallons
Volume = pi x r^2 x L
= pi x D^2 x L/4
= (pi x (0.5ft)^2 x 5280ft)/4 x 7.48 gal/ft^3
= 7750 Gallons
Eleven Steps to determine Log Inactivation
Step 1 – Determine Peak Flow
Step 2 – Determine Effective Volume
Step 3 – Determine the Baffling Factor
Step 4 – Calculate the Corrected Volume
Step 5 – Calculate the Contact Time
Step 6 – Determine Free Chlorine Concentration
Step 7 – Calculate the CT Value
Step 8 – Determine the pH
Step 9 – Determine the Temperature
Step 10 – Determine CT required to
Obtain 1.0 Log Inactivation
Step 11 – Calculate the Log Inactivation
Step 1 Determin Peak Flow
Maximum flow through the plant during the day or week.
Consider raw water flow rate, including backwash decant water.
Consider distribution pumps
Backwash pumps that draw out of the clearwell must be considered
Must be in Gallons per Minute (gpm)
To Convert Million Gallons per Day (MGD) to Gallons per Minute (gpm), multiply by 694.4
Example: 2.1 MGD
2.1 MGD x 694.4 = 1,458 gpm
2,100,000 gallons per day/ 1440 minutes per day = 1,458 gpm
Step 3 Determine Baffling Factor
*Based on hydraulic detention time at minimum operating depth.
Pipeline flow
1.0
Perfect (plug flow)
Serpentine baffling throughout basin
0.9
Excellent
Perforated inlet baffle, serpentine or perforated intra-basin baffles, outlet weir or perforated weir
0.7
Superior
Baffled inlet or outlet with some intra-basin baffling
0.5
Average
Single or multiple unbaffled inlets and outlets no intra-basin baffles
0.3
Poor
None; agitated basin, high inlet and outlet flow velocities, variable water level
0.1
Unbaffled
Baffling Description
Factor
Baffling Condition
Unbaffled
bf = 0.1
IN
OUT
Poor Baffling
bf = 0.3
OUT
IN
Average Baffling
bf = 0.5
OUT
IN
Poor Baffling
bf = 0.3
Superior Baffling
bf = 0.7
OUT
IN
Superior Baffling
bf = 0.7
IN
IN
OUT
OUT
Excellent Baffling
bf = 0.9
OUT
IN
Step 4 Calculate the Corrected Volume
Corrected Volume = Effective Volume x Baffling Factor
Example:
Corrected Volume = 750,000 gal x 0.3
= 225,000 gal
Step 5 Calculate the Contact Time
Contact Time = Corrected Volume / Peak Instantaneous Flow
Example:
Contact Time = 225,000 gal / 7,500 gpm
= 30 min
Step 6 Determine Free Chlorine Concentration
Free Chlorine Residual (mg/l)
The free chlorine residual concentration is the amount of chlorine in the water that has not reacted/combined with any organic materials or compounds.
This is different than total chlorine residual, which is the sum of the combined and free chorine residuals.
The free chorine residual must be sampled at the end of each disinfection segment, preferably during the peak hourly flow.
Step 7 Calculate the CT Value
Actual CT Value = Free Chlorine Conc. x Contact Time
Example: Free Chlorine Conc. = 2.0 mg/l
Contact Time = 30 min
CTactual = 2.0 mg/l x 30 min
= 60 mg-min/l
Step 8 Determine the pH
Measure the pH at the end of the basin
Same place you measure for free chlorine
Step 9 Determine the water temperature
Measure the Temperature at the end of the basin
Temperature in degrees Celisus
Same place you measure for free chlorine
Step 10 Determine CT required to obtain 1 Log Inactivation
Tables for 1-Log inactivation of Giardia are included.
To use these tables,
begin by locating your temperature on the top of one of the tables.
On this same table, locate your pH value.
Locate your chlorine residual concentration. (To be conservative, choose from the chart a chlorine residual that is rounded to the next highest even tenth
Read CT1-log Value
Step 11 Calculate the Log Inactivation
Log Inactivation = CTactual / CT1-log
Example:
Log Inactivation = (60 mg-min/l) / (50 mg-min/l)
= 1.2 Log Inactivation of Giardia
Use the following:
Peak design flow rate
Low water mark for all basins
Lowest pH of the water in the basin
(This may require setting a target pH
coldest temperature 5ºC)
Accurate baffling
Superior Baffling
bf = 0.7
IN
OUT

## CT Profile Calculator
CT Profile Calculator and Log
Overview
This spreadsheet will automatically determine the log inactivation of Giardia cysts and viruses by your system's disinfection process. Log inactivations can be determined and logged for up to six (6) disinfection segements.
A disinfection segement is defined as a section of a treatment system beginning at one disinfectant injection or monitoring point and ending at the next disinfectant injection or monitoring point. Every disinfectant injection point is the start of a new disinfection segment. Every injection point has an associated monitoring point.
Systems serving less than 10,000 people should calculate log inactivations weekly.
System serving more than 10,000 people should caluclate log inativations daily.

## Entry Form
Disinfection Profile |  | Please Enter Data in YELLOW cells only!
Baffling Condition | Baffling Factor (T10/T) | Baffling Description |  |  | Example
Unbaffled (mixed flow) | 0.1 | None, agitated basin, very low length to width ratio, high inlet & outlet velocities |  |  | Rapid Mix Basin
Poor | 0.3 | Single or multiple unbaffled inlets and outlets, no intrabasin baffles |  |  | Clearwell
Average | 0.5 | Baffled inlet or outlet with some intra-basin baffles |  |  | Sedimentation Basin
Superior | 0.7 | Perforated inlet baffle, serpentine or perforated intra-basin baffles, outlet weir or perforated launders |  |  | Filters
Perfect (plug flow) | 1 | Very high length to width ratio (pipeline flow), perforated inlet, outlet and intrabasin baffles |  |  | Pipe
PWSID No. | Today's Date
2023-10-20
| Basin 1 | Basin 2 | Basin 3 | Basin 4 | Basin 5 | Basin 6
Effective Basin Size (gal.)
Baffling Factor (T10/T) | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Disinfection Method | bar: 2023-10-20 Basin 1 to 2023-10-20 Basin 6
Peak Flow Rate (gpm)
Disinfectant Conc. (mg/L) | [6 empty] | Total Log Inactivation
pH (s.u.) Range = 6.0 to 9.0
Temperature (oC) Range = 1 to 25 oC
Contact Time T10 (minutes)
CTCalc
CT99.9 (Giardia)
Log Inactivation (G) | [6 empty] | 0
CT99.9 (Viruses)
Log Inactivation (V) | [6 empty] | 0
Transfer Data to Entry Log Sheets (Don't forget to save)

## Entry Log 1
Basin 1
Date | Peak Flow Rate | Disinfectant Concentration | pH | Temperature | Log Inactivation (G) | Log Inactivation (V)

## Entry Log 2
Basin 2
Date | Peak Flow Rate | Disinfectant Concentration | pH | Temperature | Log Inactivation (G) | Log Inactivation (V)

## Entry Log 3
Basin 3
Date | Peak Flow Rate | Disinfectant Concentration | pH | Temperature | Log Inactivation (G) | Log Inactivation (V)

## Entry Log 4
Basin 4
Date | Peak Flow Rate | Disinfectant Concentration | pH | Temperature | Log Inactivation (G) | Log Inactivation (V)

## Entry Log 5
Basin 5
Date | Peak Flow Rate | Disinfectant Concentration | pH | Temperature | Log Inactivation (G) | Log Inactivation (V)

## Entry Log 6
Basin 6
Date | Peak Flow Rate | Disinfectant Concentration | pH | Temperature | Log Inactivation (G) | Log Inactivation (V)

## Entry Log Total
Total
Date | Log Inactivation (G) | Log Inactivation (V)

## Sheet4 (hidden)
CT Values for inactivation of viruses , pH 6.0-9.0
| Chlorine | Chloramines | Chlorine Dioxide | Ozone
0.5 | 12
1 | 11.6 | 2883 | 50.1 | 1.8
2 | 10.7 | 2659 | 45.9 | 1.65
3 | 9.8 | 2436 | 41.8 | 1.5
4 | 8.9 | 2212 | 37.6 | 1.35
5 | 8 | 1988 | 33.4 | 1.2
6 | 7.6 | 1889 | 31.7 | 1.16
7 | 7.2 | 1789 | 30.1 | 1.12
8 | 6.8 | 1690 | 28.4 | 1.08
9 | 6.4 | 1590 | 26.8 | 1.04
10 | 6 | 1491 | 25.1 | 1
11 | 5.6 | 1392 | 23.4 | 0.92
12 | 5.2 | 1292 | 21.7 | 0.84
13 | 4.8 | 1193 | 20.1 | 0.76
14 | 4.4 | 1093 | 18.4 | 0.68
15 | 4 | 994 | 16.7 | 0.6
16 | 3.8 | 944 | 15.9 | 0.58
17 | 3.6 | 895 | 15 | 0.56
18 | 3.4 | 845 | 14.2 | 0.54
19 | 3.2 | 796 | 13.3 | 0.52
20 | 3 | 746 | 12.5 | 0.5
21 | 2.8 | 696 | 11.7 | 0.46
22 | 2.6 | 646 | 10.9 | 0.42
23 | 2.4 | 597 | 10 | 0.38
24 | 2.2 | 547 | 9.2 | 0.34
25 | 2 | 497 | 8.4 | 0.3

## Sheet3 (hidden)
| Chloramine | Chlorine Dioxide | Ozone
1 | 3800 | 63 | 2.9 | Chlorine | 1
2 | 3400 | 53.8 | 2.65 | Chloramine | 2
3 | 3000 | 44.5 | 2.4 | Chlorine Dioxide | 3
4 | 2600 | 35.3 | 2.15 | Ozone | 4
5 | 2200 | 26 | 1.9
6 | 2130 | 25.4 | 1.81
7 | 2060 | 24.8 | 1.71
8 | 1990 | 24.2 | 1.62
9 | 1920 | 23.6 | 1.52
10 | 1850 | 23 | 1.43
11 | 1780 | 22.2 | 1.33
12 | 1710 | 21.4 | 1.24
13 | 1640 | 20.6 | 1.14
14 | 1570 | 19.8 | 1.05
15 | 1500 | 19 | 0.95
16 | 1420 | 18.2 | 0.9
17 | 1340 | 17.4 | 0.86
18 | 1260 | 16.6 | 0.81
19 | 1180 | 15.8 | 0.77
20 | 1100 | 15 | 0.72
21 | 1030 | 14.2 | 0.67
22 | 960 | 13.4 | 0.62
23 | 890 | 12.6 | 0.58
24 | 820 | 11.8 | 0.53
25 | 750 | 11 | 0.48