[Type Water System Name Here]

OPERATION AND MAINTENANCE PLAN

Template Version July 2025

# CHANGE HISTORY

This table records the changes made to this plan since its original development, who made the changes and on what date the changes were incorporated into this plan.

| description of change | NAME/TITLE | Date |
| --- | --- | --- |
| Creation of Plan |  |  |

# GOVERNING BOARD APPROVAL STATEMENT

The governing board of [Water System Name] has reviewed this Operations and Maintenance (O&M) plan and hereby certifies that all the information contained within this document is true to the best of our knowledge. This document shall serve as a comprehensive informational reference for water system operations and maintenance knowledge. The [Water System Name] board approves of this O&M and its contents.

| Board Member Name (Print) |  | Board Member Position |
| --- | --- | --- |
| Board Member Name (Sign) |  | Date |

# TABLE OF CONTENTS – Right click and select “update field” to update the table of contents

CHANGE HISTORY	a

GOVERNING BOARD APPROVAL STATEMENT	b

TABLE OF CONTENTS	c

1.	OVERVIEW OF FACILITIES	1

1.1	Utility Overview	1

1.2	Responsible Officials	1

1.3	Service Area/Source Map(s)	2

1.4	Treatment System Schematic	2

1.5	Permit Information	2

2.	SOURCE INFORMATION	3

2.1	Well(s)	3

2.1.i	Well Pump(s)	4

2.2	Spring(s)	5

2.3	Purchased Water	6

2.4	High Service or Booster Pump(s)	7

2.5	Master Meter Records	8

3.	TREATMENT SYSTEM	9

3.1	Disinfection	9

3.1.i	Other Treatment	10

4.	DISTRIBUTION SYSTEM	11

4.1	Distribution System Overview	11

4.2	Finished Water Storage	12

4.3	Raw Water Storage	13

5.	OPERATIONAL PROCEDURES	14

5.1	Start up and Shutdown	14

5.2	Disinfection Operations	14

5.3	Operating Procedures	15

5.3.i	Start-up Operating Procedure	15

5.3.ii	Disinfection Procedure	15

5.3.iii	Emergency Shutdown Procedure	15

5.3.iv	Flushing Procedure	15

5.3.v	Meter Reading Procedure	15

5.3.vi	Other Procedure	16

5.3.vii	Other Procedure	16

5.4	Operating Conditions	17

5.4.i	Normal Operating Conditions	17

5.5	Emergency Operating Conditions	17

6.	MAINTENANCE/REPAIR PRACTICES	18

6.1	Maintenance/Repair Contacts	18

6.2	Repairs and Work Orders	18

6.3	Preventative Maintenance	18

6.3.i	Flushing	19

6.3.ii	Elimination of Cross-Connections	19

6.3.iii	Meter Calibration	20

6.3.iv	Regular Valve Exercising	20

6.4	Water Main and Service Line Repairs	20

6.5	Safety Equipment Maintenance/Repairs	20

7.	Active Inventory Records	22

7.1	Active Inventory	22

7.2	Standard Chemical Inventory	22

7.3	Standard Piping Inventory	22

8.	Sampling, Monitoring, and Reporting	23

8.1	Sampling, Monitoring, Reporting Checklist	23

8.1.i	Continuous Meters	23

8.1.ii	Grab Sampling	23

8.2	On-site Lab Equipment	24

8.3	External Testing Services	24

9.	Public Notification Requirements	25

9.1	Notification Levels	25

9.2	Required Elements of a Public Notice	26

9.2.i	Standard Language Examples	26

Appendix A. Blank Forms and Records	27

Appendix B. Active Records	34

Appendix C. Emergency Response Plan (ERP)	35

# OVERVIEW OF FACILITIES

## Utility Overview

| PWSID |  |
| --- | --- |
| System Name |  |
| Primary Source Type |  |
| Street Address |  |
| City, State Zip Code |  |
| Utility Phone number |  |
| Population Served |  |
| Prepared by (Utility representative) |  |
| Reviewed by (if applicable) |  |
| Date completed |  |

## Responsible Officials

Utility team members who are responsible for the organization and operation of the water system.

| Name | Title | Contact Information |
| --- | --- | --- |

## Service Area/Source Map(s)

The storage location of service area maps and the date of their last known update.

| Map name | Location | Last updated on: |
| --- | --- | --- |
| Distribution System Map(s) |  |  |
| Source/Intake Map(s) - (indicates raw water transmission lines to plant) |  |  |

## Treatment System Schematic

Is the treatment system schematic included in this O&M? If so, what is included in the schematic?

| Is the Treatment System Schematic Attached? |  | Yes ☐ No ☐ |
| --- | --- | --- |
| Schematic Indicates: (check all that apply) | ☐ Sources of Supply ☐ Master Meters ☐ Raw Water Taps ☐ Valves ☐ Finished Water Taps ☐ Contacts Tanks ☐ Chemical Treatment Injection Points ☐ Entry Points |  |

## Permit Information

List of water system permit information including date issued, purpose, and location of key documents.

| Permit No. | Date Issued | Purpose | Location of Documents |
| --- | --- | --- | --- |

# SOURCE INFORMATION

## Well(s)

The tables below provide information regarding each well utilized by the water system.

| Well identification: |  |  |  |
| --- | --- | --- | --- |
| Permit No. |  |  |  |
| Date of Permit |  |  |  |
| Location |  |  |  |
| Date Drilled |  |  |  |
| Diameter (in.) |  | Total Well Depth (ft) |  |
| Casing Diameter (in) |  | Casing Length (ft) |  |
| Pumping Capacity (gpm) |  |  |  |
| Static Water Level (ft) |  | Pumping Water Level (ft) |  |

| Well identification: |  |  |  |
| --- | --- | --- | --- |
| Permit No. |  |  |  |
| Date of Permit |  |  |  |
| Location |  |  |  |
| Date Drilled |  |  |  |
| Diameter (in.) |  | Total Well Depth (ft) |  |
| Casing Diameter (in) |  | Casing Length (ft) |  |
| Pumping Capacity (gpm) |  |  |  |
| Static Water Level (ft) |  | Pumping Water Level (ft) |  |

### Well Pump(s)

The tables below provide information regarding each of the water system’s well pumps.

| Well pump identification: |  |
| --- | --- |
| Type of Pump |  |
| Manufacturer/Model |  |
| Capacity (gpm) |  |
| Horsepower (hp) |  |
| Pump Setting (depth) |  |
| Controls |  |

| Well pump identification: |  |
| --- | --- |
| Type of Pump |  |
| Manufacturer/Model |  |
| Capacity (gpm) |  |
| Horsepower (hp) |  |
| Pump Setting (depth) |  |
| Controls |  |

## Spring(s)

The table(s) below provide details for each spring within the distribution system.

| Spring name: |  |
| --- | --- |
| Permit No. |  |
| Date of Permit |  |
| Location |  |
| Capacity (gpm) |  |
| Collection Basin Construction |  |

| Spring name: |  |
| --- | --- |
| Permit No. |  |
| Date of Permit |  |
| Location |  |
| Capacity (gpm) |  |
| Collection Basin Construction |  |

## Purchased Water

The tables below provide information regarding each interconnection utilized by the water system.

| Interconnection Name: |  |  |  |
| --- | --- | --- | --- |
| Address |  |  |  |
| Contact information |  |  |  |
| Agreement Date |  |  |  |
| Max Capacity (gpd) |  |  |  |
| Pressure (psi) |  |  |  |
| Metered | Yes ☐ No ☐ | Meter size (in) |  |
| Average day (gpd) |  |  |  |
| Backflow Preventer | Yes ☐ No ☐ |  |  |
| Additional Treatment | Yes ☐ No ☐ |  |  |
| Treatment includes |  |  |  |
| Additional Information |  |  |  |

| Interconnection Name: |  |  |  |
| --- | --- | --- | --- |
| Address |  |  |  |
| Contact information |  |  |  |
| Agreement Date |  |  |  |
| Max Capacity (gpd) |  |  |  |
| Pressure (psi) |  |  |  |
| Metered | Yes ☐ No ☐ | Meter size (in) |  |
| Average day (gpd) |  |  |  |
| Backflow Preventer | Yes ☐ No ☐ |  |  |
| Additional Treatment | Yes ☐ No ☐ |  |  |
| Treatment includes |  |  |  |
| Additional Information |  |  |  |

## High Service or Booster Pump(s)

The table(s) below provide details for each high service or booster pump within the water system.

| Pump Identification: |  |  |  |
| --- | --- | --- | --- |
| Size (in) |  | Capacity (gpm) |  |
| Head (ft) |  | Pump Specs Attached | Yes ☐ No ☐ |
| Manufacturer & Model No |  |  |  |
| Impeller Diameter (in) |  | Pump Curve |  |
| Suction Pressure (psi) |  | Discharge Pressure (psi) |  |
| Metered | Yes ☐ No ☐ |  |  |
| Motor Manufacturer & No. |  |  |  |
| Horsepower |  | RPM |  |
| Volts |  | Amps |  |
| Controls/other information |  |  |  |

| Pump Identification: |  |  |  |
| --- | --- | --- | --- |
| Size (in) |  | Capacity (gpm) |  |
| Head (ft) |  | Pump Specs Attached | Yes ☐ No ☐ |
| Manufacturer & Model No |  |  |  |
| Impeller Diameter (in) |  | Pump Curve |  |
| Suction Pressure (psi) |  | Discharge Pressure (psi) |  |
| Metered | Yes ☐ No ☐ |  |  |
| Motor Manufacturer & No. |  |  |  |
| Horsepower |  | RPM |  |
| Volts |  | Amps |  |
| Controls/other information |  |  |  |

## Master Meter Records

Details regarding each Master Meter within the water system.

| Master Meter ID: |  |  |  |
| --- | --- | --- | --- |
| Location |  |  |  |
| Size |  | Type |  |
| Units | gpm ☐ cfm ☐ | Chart | Yes ☐ No ☐ |
| Last Calibration Date |  | Frequency of Calibration |  |

| Master Meter ID: |  |  |  |
| --- | --- | --- | --- |
| Location |  |  |  |
| Size |  | Type |  |
| Units | gpm ☐ cfm ☐ | Chart | Yes ☐ No ☐ |
| Last Calibration Date |  | Frequency of Calibration |  |

| Master Meter ID: |  |  |  |
| --- | --- | --- | --- |
| Location |  |  |  |
| Size |  | Type |  |
| Units | gpm ☐ cfm ☐ | Chart | Yes ☐ No ☐ |
| Last Calibration Date |  | Frequency of Calibration |  |

| Master Meter ID: |  |  |  |
| --- | --- | --- | --- |
| Location |  |  |  |
| Size |  | Type |  |
| Units | gpm ☐ cfm ☐ | Chart | Yes ☐ No ☐ |
| Last Calibration Date |  | Frequency of Calibration |  |

# TREATMENT SYSTEM

## Disinfection

Details regarding any disinfection that occurs within the water system.

| Disinfection Treatment Method 1 |  |  |  |
| --- | --- | --- | --- |
| Chemical Used |  |  |  |
| Strength (%) |  | Size Container (gal/lb) |  |
| Chemical Supplier |  |  |  |
| Phone of Supplier |  |  |  |
| Type of Chemical Feeder |  |  |  |
| Equipment No. |  | Model No. |  |
| Capacity (gpd) |  | Pressure (psi) |  |
| Feeder Specs Attached? | Yes ☐ No ☐ |  |  |
| Feeder is Equipped With: (check all that apply) | ☐ Pressure Relief Valve ☐ Calibration Chamber ☐ Anti-siphon Valve ☐ De-gassing Valve ☐ Backpressure Valve ☐ Foot Valve |  |  |
| Chlorine Contact Time (mins) |  | At Flow Rate (gpm) |  |
| Contact Tank or Clearwell Volume (gal) |  |  |  |
| Transmission Pipe Diameter (in) |  | Transmission Pipe Length (ft) |  |
| Controls (manual, auto, ...) |  |  |  |

### Other Treatment

Details regarding any additional treatment methods used within the treatment system.

| Additional Treatment: |  |  |  |
| --- | --- | --- | --- |
| Purpose |  |  |  |
| Chemical Used |  |  |  |
| Strength (%) |  | Size Container (gal/lb) |  |
| Chemical Supplier |  |  |  |
| Phone of Supplier |  |  |  |
| Type of Chemical Feeder |  |  |  |
| Manufacturer |  |  |  |
| Equipment No. |  | Model No. |  |
| Capacity (gpd) |  | Pressure (psi) |  |
| Feeder Specs Attached? | Yes ☐ No ☐ |  |  |
| Feeder is Equipped With: (check all that apply) | ☐ Pressure Relief Valve ☐ Calibration Chamber ☐ Anti-siphon Valve ☐ De-gassing Valve ☐ Backpressure Valve ☐ Foot Valve |  |  |
| Method Used for Process Control |  |  |  |

# DISTRIBUTION SYSTEM

## Distribution System Overview

| Location of Distribution Map |  |  |  |  |
| --- | --- | --- | --- | --- |
| Distribution Map Indicates: (check all that apply) | ☐ Pipe Material ☐ Pipe Length ☐ Pipe Diameter ☐ Valves ☐ Fire Hydrants ☐ Dead Ends |  |  |  |
| Valves Open (indicate) | ☐ Left ☐ Right |  |  |  |
| Fire Hydrants Open (indicate) | ☐ Left ☐ Right |  |  |  |
| Pressure Regulating Valve |  |  |  |  |
| Location |  |  |  |  |
| Manufacturer |  | Size (in) |  |  |
| Do you maintain records of residential meters? |  | Yes ☐ No ☐ |  |  |
| Where are they located? |  |  |  |  |
| Do you maintain an inventory of distribution materials? (i.e. pipes, valves) |  |  | Yes ☐ No ☐ |  |
| Where is it located? |  |  |  |  |

## Finished Water Storage

Details for each finished water storage facility and its associated pressure tank(s) if applicable.

| Name of Storage Asset: |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Type of Storage |  |  |  |  |  | Capacity (gal) |  |  |  |  |  |
| Location |  |  |  |  |  |  |  |  |  |  |  |
| If Elevated Tank: | Height (ft) |  |  |  | Diameter (ft) |  |  |  |  |  |  |
| If Reservoir: | Length (ft) |  |  |  | Width (ft) |  |  |  | Depth (ft) |  |  |
| Elevations: | Base (ft) |  |  |  |  |  | Overflow (ft) |  |  |  |  |
| Pipe Size: | Inlet (in) |  |  |  |  |  | Outlet (in) |  |  |  |  |
| Year Constructed |  |  |  |  |  |  |  |  |  |  |  |
| Tank Manufacturer |  |  |  |  |  |  |  |  |  |  |  |
| Manufacturer Phone |  |  |  |  |  |  |  |  |  |  |  |
| Type of Foundation |  |  |  |  | Type of Construction |  |  |  |  |  |  |
| Type of Paint System |  |  |  |  |  |  |  |  |  |  |  |
| Storage Facility is Equipped with: (check all that apply) | ☐ Fence ☐ Float Gauge ☐ Exterior Ladder ☐ Drain Pipe ☐ Pump Controls ☐ Altitude Valve ☐ Interior Ladder ☐ Overflow Pipe ☐ Water Level Recorder |  |  |  |  |  |  |  |  |  |  |

| Pressure Tank ID: |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Location |  |  |  |  |  |  |  |  |  |
| Manufacturer |  |  |  | Spec Sheet Attached? |  |  |  | Yes ☐ No ☐ |  |
| Manufacturer Address |  |  |  |  |  |  |  |  |  |
| Manufacturer Phone |  |  |  |  |  |  |  |  |  |
| Size of Tank | Diameter (ft) |  |  |  |  | Height (ft) |  |  |  |
| Percent Air (ft) |  |  |  |  |  |  |  |  |  |
| Pressure Range (psi) |  |  |  |  | - |  |  |  |  |

## Raw Water Storage

Details for each raw water storage facility and its associated pressure tank(s) if applicable.

| Name of Storage Asset: |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Type of Storage |  |  |  |  |  | Capacity (gal) |  |  |  |  |  |
| Location |  |  |  |  |  |  |  |  |  |  |  |
| If Elevated Tank: | Height (ft) |  |  |  | Diameter (ft) |  |  |  |  |  |  |
| If Reservoir: | Length (ft) |  |  |  | Width (ft) |  |  |  | Depth (ft) |  |  |
| Elevations: | Base (ft) |  |  |  |  |  | Overflow (ft) |  |  |  |  |
| Pipe Size: | Inlet (in) |  |  |  |  |  | Outlet (in) |  |  |  |  |
| Year Constructed |  |  |  |  |  |  |  |  |  |  |  |
| Tank Manufacturer |  |  |  |  |  |  |  |  |  |  |  |
| Manufacturer Phone |  |  |  |  |  |  |  |  |  |  |  |
| Type of Foundation |  |  |  |  | Type of Construction |  |  |  |  |  |  |
| Type of Paint System |  |  |  |  |  |  |  |  |  |  |  |
| Storage Facility is Equipped with: (check all that apply) | ☐ Fence ☐ Float Gauge ☐ Exterior Ladder ☐ Drain Pipe ☐ Pump Controls ☐ Altitude Valve ☐ Interior Ladder ☐ Overflow Pipe ☐ Water Level Recorder |  |  |  |  |  |  |  |  |  |  |

| Pressure Tank ID: |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Location |  |  |  |  |  |  |  |  |  |
| Manufacturer |  |  |  | Spec Sheet Attached? |  |  |  | Yes ☐ No ☐ |  |
| Manufacturer Address |  |  |  |  |  |  |  |  |  |
| Manufacturer Phone |  |  |  |  |  |  |  |  |  |
| Size of Tank | Diameter (ft) |  |  |  |  | Height (ft) |  |  |  |
| Percent Air (ft) |  |  |  |  |  |  |  |  |  |
| Pressure Range (psi) |  |  |  |  | - |  |  |  |  |

# OPERATIONAL PROCEDURES

## Start up and Shutdown

What controls the start-up of your water source? (Automatic? Manual? If automatic, what activates the pump? Pressure switch? Level controls?)

What controls the shut-down of your water source? (Automatic? Manual? Pressure drop? At what pressure does the pump shut off?)

What controls water levels in the tank or reservoir? (Altitudes valve, float, pressure?)

## Disinfection Operations

▪ What controls the start-up and shutdown of the chlorinator?

▪ What controls the chlorine dosage? (i.e. automatic, analyzer)

▪ How often are the pumps & controls checked for proper operation?

| ▪ What chemical is fed? |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ▪ If liquid, what is the product strength (as delivered)? |  |  |  |  |  | lbs/gal |  |
| ▪ Is the solution diluted in a day tank? |  |  | Yes ☐ No ☐ |  |  |  |  |
| ▪ Procedure: |  | gallons of liquid chlorine is mixed with |  |  |  |  | gallons of water |
| ▪ What is the product strength of the solution fed? |  |  |  |  |  | lbs/gal |  |
| ▪ What is the residual normally retained? |  |  |  |  |  | mg/L |  |
| ▪How do you measure the residual? (How often, where, when, etc.) |  |  |  |  |  |  |  |

## Operating Procedures

Step by step procedures on various operations for the water system.

### Start-up Operating Procedure

      - Step 1...

      - Step 2...

      - Step 3...

### Disinfection Procedure

      - Step 1...

      - Step 2...

      - Step 3...

### Emergency Shutdown Procedure

      - Step 1...

      - Step 2...

      - Step 3...

### Flushing Procedure

      - Step 1...

      - Step 2...

      - Step 3...

### Meter Reading Procedure

      - Step 1...

      - Step 2...

      - Step 3...

### Other Procedure

      - Step 1...

      - Step 2...

      - Step 3...

### Other Procedure

      - Step 1...

      - Step 2...

      - Step 3...

Add any additional procedures or alter any of the above

## Operating Conditions

### Normal Operating Conditions

These are the normal operating procedures/checkpoints for the facility

| ▪ Normal quantity of water produced per day | Average |  | Maximum |  |
| --- | --- | --- | --- | --- |
| ▪ Normal quantity of water produced (GPM) | Average |  | Maximum |  |
| ▪ Normal total operating hours per day | Average |  | Maximum |  |
| ▪ Plant pressures (psi) | Minimum |  | Maximum |  |
| ▪ Entry Point chlorine residual (ppm) | Minimum |  | Maximum |  |

▪ Distribution system chlorine residuals (ppm):

| Location | Minimum-free | / | Total | Maximum-free | / | Total |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | / |  |  | / |  |
|  |  | / |  |  | / |  |
|  |  | / |  |  | / |  |
|  |  | / |  |  | / |  |

▪ Distribution system pressures:

| Location | Minimum (psi) | Maximum (psi) |
| --- | --- | --- |

## Emergency Operating Conditions

An emergency exists when the following conditions are true.

| The flow leaving the plant exceeds: |  | GPM |
| --- | --- | --- |
| The entry point chlorine residual is less than: |  | ppm |
| The water pressure falls below: |  | psi |
| Other condition(s): |  |  |

# MAINTENANCE/REPAIR PRACTICES

## Maintenance/Repair Contacts

The following table contains contact information for all persons relevant to maintenance and repairs at the water system. This list should include the water systems own employees as well as any vendors who are contracted to perform repairs.

| Name/Title/Company | Type of Maintenance/Repair duties | Contact Information |
| --- | --- | --- |

## Repairs and Work Orders

If a component associated with the water facility needs a repair or maintenance, then a work order for the needed repair or work shall be issued and completed. A blank Work Order Form can be found in Appendix A. All completed work orders should be maintained in Appendix B (or another designated location) after completion so there is a historic record of all repairs made on the system. If completed work orders are to be maintained in a different location than this O&M, note the location:

| Location of Completed Work Orders | As of Date |
| --- | --- |

## Preventative Maintenance

The following is a list of various preventative maintenance activities that shall be performed daily, weekly, monthly, quarterly, and/or annually. These tasks will be performed to keep the system running reliably and properly.

Routine preventative maintenance should include flushing, exercising of emergency backup equipment, maintenance of safety equipment, etc. See this O&M resource from the EPA for assistance in developing the below lists: Operation & Maintenance Checklist and Tasks (epa.gov)

| Activity | Frequency | Maintenance Required |
| --- | --- | --- |
| Security Check | Daily | Inspect tower and storage shed areas to ensure no trespassing has occurred. |
| Check Chlorine Residual Levels | Daily |  |
| Read meters | Monthly | Read the customer and master meters and ensure they all make sense compared to prior readings |
| Exercising backup generators | Monthly |  |
| Exercising backup pumps | Monthly |  |
| Maintenance/inspection of safety equipment | Monthly |  |
| Flushing | Every 90 days |  |
| Review Emergency Response Plan | Annually | Ensure emergency contacts and procedures are up to date |
| Exercise valves | Annually | Rotate valves in the system to ensure working properly |

### Flushing

Dead ends should be flushed every 90 days. A schedule of flushing should be established for the system to ensure flushing activities are being performed on a routine basis. If there are automatic flush hydrants in the system, note them in the schedule as automatic flushing and note the schedule they are on. As flushing is completed, maintain a record of flushing.

The schedule and record for flushing can be found: A flushing report template can be found in Appendix A.

In Appendix B of this O&M -- On a clipboard in the office -- in a spreadsheet on the office computer saved under “__”.

The official(s) responsible for flushing are established below and are updated as needed.

| Responsible Party/Name | Phone Contact | Email Contact | As of (date) |
| --- | --- | --- | --- |

### Elimination of Cross-Connections

Elimination of cross connections is imperative in preventing the contamination of potable water supplies. Backflow, back siphonage, and siphonage can lead to cross-connections with non-potable or contaminated sources of water. If contamination is occurring, a cross-connection survey of the system should occur along with visual inspections in order to determine potential cross connections. Flow testing and pressure testing can be utilized as well to assist in determining locations of cross-connections. In the case of a cross-connection, installation of a measure to prevent contamination is necessary. Some examples include backflow preventors, check valves, air gaps, and/or vacuum breakers.

### Meter Calibration

To have an accurate measure of performance at the facility, meters should be calibrated as necessary. For meters that cannot be calibrated, they should be tested routinely and replaced as needed. Meter calibration and replacement records shall be retained and maintained either in this O&M, or in another designated location. Meter calibration records can be found: An example of a meter calibration/replacement tracker can be found in Appendix A.

In Appendix B of this O&M -- On a clipboard in the office -- in a spreadsheet on the office computer saved under “__”.

### Regular Valve Exercising

Following a regular valve exercising program, documenting discovered issues, and making timely required repairs will help ensure that isolation and main valves work when you need them. It is important to exercise all mainline valves in the system at least once a year to ensure that you can locate them and that they can be opened and closed properly during emergency shut-down periods. A record of valve exercises should be recorded in Valve Exercising Records located in Appendix B or in another location. If in another location, it is listed below. Information in the records should include the physical condition of the valve (rusted/new, leaking, failing, etc.), number and direction of turns to open and closure, any maintenance conducted, and any other observations. Any valves needing repair should have a work order placed on them. An example of a valve exercising record can be found in Appendix A.

| Location of Valve Exercising Records | On a clipboard in the office, etc. – delete this if in appendix B |
| --- | --- |

## Water Main and Service Line Repairs

Water distribution line repairs should be documented, especially when there are repairs/clamps, etc., placed on the line. These types of repairs are not normally intended for long-term/permanent repairs but are often performed with that intent. A thorough record of line replacements may help identify areas of the distribution line that are more prone to failure due to age, vibration, or other causes. Every repair of a water main or service line should be recorded in a work order.

## Safety Equipment Maintenance/Repairs

Chemicals used in water treatment, such as chlorine, can be dangerous, and it is therefore imperative that your safety equipment be carefully maintained, and that maintenance be documented. All safety equipment needs to be inventoried, and a log of the maintenance and repairs should be kept. Make sure to update the log throughout the year as repairs are made.

| Equipment Type | Location | Maintenance/Repair Performed | Performed by (Initials) | Date |
| --- | --- | --- | --- | --- |

# Active Inventory Records

## Active Inventory

An active inventory of all supplies maintained by the system should be updated on a regular basis. This inventory should include an accounting of chemicals, available piping, repair/maintenance equipment, and repair/maintenance materials. An active inventory for this water system can be found in the following location:

An example Inventory can be found in Appendix A of this O&M

| Location of Active Inventory | As of Date |
| --- | --- |
| In Appendix B of this O&M -- On a clipboard in the work shed -- in a spreadsheet on the office computer saved under “__”. |  |

## Standard Chemical Inventory

Below is a comprehensive list of the typical quantities of chemicals kept on site at the water facility. An active inventory can be found within the active inventory for the system

| Chemical Name | Use | Quantity | Location | Safety Measures (containment, etc.) |
| --- | --- | --- | --- | --- |

## Standard Piping Inventory

Below is a comprehensive list of the typical quantities of piping kept on site at the water facility.

| Pipe Type | Size | Quantity | Location |
| --- | --- | --- | --- |

# Sampling, Monitoring, and Reporting

The process control tests being performed at this facility are dependent on the treatment process, chemicals added, type of source, etc. Check with your DEQ enforcement officer and/or DEQ Water Quality Department to confirm all sampling, monitoring, and reporting requirements, or refer to SDWIS Drinking Water Watch (Drinking Water Branch (state.ok.us)).

## Sampling, Monitoring, Reporting Checklist

Below are items that should be completed to maintain data integrity and quality when sampling, monitoring, and recording of data occurs at this facility.

### Continuous Meters

- Ensure necessary flow is going through all meters.

- Ensure meters are set for the correct day and time.

- Ensure the least amount of tubing connecting the sampling point to the continuous meter is being utilized.

- Ensure sample tap is installed correctly.

- Verify that the meter is reading properly by comparing to grab samples (at least once a week).

- Calibrate meters on the frequency designated by the manufacturer recommendations (usually every 3 months – once a year).

- Designate where instruction manuals for all meters, instrumentation, and control systems (SCADAs) are maintained (and maintain them).

- Develop written operating procedures on how to navigate the control system.

  - How to set meter read caps (and be sure that all caps are high enough to have accurate readings).

  - How to set alarms

  - How to pull historical files

### Grab Sampling

- Have detailed written operating procedures on how to collect and run each type of grab sample.

  - Designate the exact location(s) of where grab samples are pulled.

  - Designate frequency based on requirements and facility best practices.

- Have several staff trained on how to sample.

- Have several staff trained on how to use testing instrumentation.

  - Develop written operating procedures for utilizing instrumentation.

- Designate where instruction manuals for all meters and instrumentation are maintained (and maintain them).

- Calibrate instrumentation regularly.

  - Ensure that all calibration reagents are not expired.

## On-site Lab Equipment

This facility shall maintain an inventory of all on-site lab equipment and an agreement with an equipment supplier so any faulty or needed equipment can be maintenanced, replaced, or obtained.

The inventory of lab equipment is located:

| Lab Equipment Supplier |  |
| --- | --- |
| Name |  |
| Address |  |
| Contact Name |  |
| Contact Phone |  |
| Account No. |  |

## External Testing Services

An external laboratory conducts the following services:

| External Services |  |  |
| --- | --- | --- |
| Lab Name |  |  |
| Address |  |  |
| Contact |  |  |
| Certified Lab No. |  |  |
| Phone No. |  |  |
| The duties of the outside lab include: |  |  |
| ☐ Sample Collection |  | ☐ Reporting to DEQ |
| ☐ Sample Analyses |  | ☐ Other: |
| ☐ Reporting to System |  |  |
| Outside laboratory analyses include (check those that apply): |  |  |
| ☐ Coliform Bacteria |  | ☐ SOCs |
| ☐ IOCs |  | ☐ Radiological |
| ☐ VOCs |  | ☐ Other: |
| ☐ TTHMs |  |  |

# Public Notification Requirements

## Notification Levels

Under the Public Notification Rule of the Safe Drinking Water Act, public water supplies must notify customers if there is a risk to public health with the drinking water, within designated time frames based on the health risk. These notices must be provided to all persons served, and not just billed customers.

| TIER 1 | Immediate Notice - Within 24 hours of violation/situation |
| --- | --- |
| Notification Method: Radio, TV, hand delivery, posting, or other method specified by the primacy agency. PWSs must also initiate consultation with the primacy agency within 24 hours. |  |
| - Distribution system sample violation when fecal coliform or E. coli are present; failure to test for fecal coliform or E. coli after initial total coliform distribution system sample tests positive. - Nitrate, nitrite, or total nitrate and nitrite maximum contaminant level (MCL) violation; failure to take confirmation sample. - Special notice for noncommunity water systems (NCWSs) with nitrate exceedances between 10 mg/L and 20 mg/L, where system is allowed to exceed 10 mg/L by primacy agency. - Chlorine dioxide maximum residual disinfectant level (MRDL) violation when one or more of the samples taken in the distribution system exceeds the MRDL on the day after a chlorine dioxide measurement taken at the entrance to the distribution system exceeds the MRDL, or when required samples are not taken in the distribution system. - Exceedance of maximum allowable turbidity level, if elevated to a Tier 1 notice by agency. - Waterborne disease outbreak or other waterborne emergencies. - Detection of E. coli, enterococci, or coliphage in a ground water source sample. |  |
| TIER 2 | Notice as Soon as Practical – Within 30 Days |
| Notification Method: Mail or other direct delivery, and any other method as needed to reach others. |  |
| - All MCL, MRDL, and treatment technique violations, except where Tier 1 notice is required. - Monitoring violations, if elevated to Tier 2 notice by primacy agency. - Failure to comply with variance and exemption conditions. - For ground water systems providing 4-log treatment and conducting Ground Water Rule (GWR) compliance monitoring, failure to maintain required treatment for more than 4 hours. - Failure to take any required corrective action or be in compliance with a corrective action plan for a fecal indicator-positive ground water source sample. - Failure to take any required corrective action or be in compliance with a corrective action plan for a significant deficiency under the GWR. - Special public notice for repeated failure to conduct monitoring for Cryptosporidium |  |
| TIER 3 | Notice within 12 month – Annual Notice |
| Notification Method: Mail or other direct delivery, and any other method as needed to reach others. |  |
| - All monitoring or testing procedure violations, unless primacy agency elevates to Tier 2, including failure to conduct benchmarking and profiling (surface water systems) and failure to develop a monitoring plan (disinfecting systems). - Operating under a variance and exemption. - Special public notice for availability of unregulated contaminant monitoring results. - Special public notice for fluoride secondary maximum contaminant level (SMCL) exceedance. |  |

## Required Elements of a Public Notice

Unless otherwise specified in the regulations, each notice must contain:

- Description of the violation or situation, including the contaminant(s) of concern, and (as applicable) the contaminant level(s).

- When the violation or situation occurred (i.e., date the sample was collected or was supposed to be collected).

- Any potential adverse health effects from drinking the water and standard language regarding the violation or situation. (For monitoring and testing procedure violations, use the example standard monitoring language below.)

- The population at risk, including subpopulations that may be particularly vulnerable if exposed to the contaminant in their drinking water.

- Whether alternate water supplies should be used.

- Actions consumers should take, including when they should seek medical help, if known.

- What the PWS is doing to correct the violation or situation.

- When the PWS expects to return to compliance or resolve the situation.

- The name, business address, and phone number or those of a designee of the PWS as a source of additional information concerning the notice.

- A statement encouraging notice recipients to distribute the notice to others, where applicable.

### Standard Language Examples

Standard Monitoring Language: We are required to monitor your drinking water for specific contaminants on a regular basis. Results of regular monitoring are an indicator of whether or not our drinking water meets health standards. During [period] we [did not monitor or test/did not complete all monitoring or testing] for [contaminant(s)], and therefore cannot be sure of the quality of the drinking water during that time.

Standard Distribution Language: Please share this information with all the other people who drink this water, especially those who may not have received this notice directly (for example, people in apartments, nursing homes, schools, and businesses). You can do this by posting this notice in a public place or distributing copies by hand or mail.

# Appendix A. Blank Forms and Records

- Work Order Form

- Flushing Report Template

- Meter Calibration/Replacement Record

- Valve Exercising Record

- Example Inventory

| Work Order |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Work Order No. |  |  |  |  |  |  |  |  | Date Work Order Created |  |  |  |  |  |  | Date Work Due |  |  |  |  |  |  |  |  |
| Requested By |  |  |  |  |  |  |  |  | Phone Number |  |  |  |  |  |  | Email |  |  |  |  |  |  |  |  |
| Asset(s) Involved |  |  |  |  |  |  |  |  |  |  |  |  |  | Location |  |  |  |  |  |  |  |  |  |  |
| Nature of Problem: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Job Started |  |  |  |  |  |  |  |  |  |  |  |  | Job Completed |  |  |  |  |  |  |  |  |  |  |  |
|  |  | MM |  | DD |  | YYYY |  |  |  |  | Time |  |  |  |  |  | MM | DD |  |  | YYYY |  | Time |  |
| Materials |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Labor |  |  |  |  |  |  |  |  |  |
| Stock No. | Item |  |  |  | Qty. |  | Unit Price |  |  |  |  | Total |  |  | Name | Reg. Hours |  |  | O.T. Hours |  |  | Rate |  | Total |
| Total |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Total |  |  |  |  |  |  |  |  |  |
| Outside Contractor Required: |  |  |  |  |  |  |  | ☐ Yes ☐ No |  |  |  |  |  |  | If yes, Contractor Cost: |  |  |  |  |  |  |  |  |  |
| What was the issue? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| How was It fixed? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Apparent cause of the issue? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Additional Remarks: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Work Completed By: |  |  | Print Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Date: |  |  |  |
|  |  |  | Sign Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Flushing Report |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date | ID # | Location | Start Time | Stop Time | Total Min | Flow GPM | Gallons Used | Static PSI | Cl2 Res | Comments | Initials |

| Meter Maintenance Report |  |  |  |  |
| --- | --- | --- | --- | --- |
| Meter ID | Calibrated or Replaced? | Date | Completed by (name) | Date of Next Calibration |

| Valve Exercising Record |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Water Supplier: |  |  |  |  |  |  |  |  | Location: |  |  |  |  |
| Valve # |  |  |  | Make |  |  |  | Size |  |  |  | Direction to Open | ☐ R ☐ L |
| Date installed |  |  |  |  |  |  |  | Installed By |  |  |  |  |  |
| Date Inspected |  | Condition |  |  | Turns to Open |  | Turns to Close |  | Maintenance and Remarks |  |  |  | Done By: |

| Active Inventory Includes chemicals, pipe, repair equipment, maintenance materials, spare parts, and back-up equipment. |  |  |  |
| --- | --- | --- | --- |
| Updated as of: _____________________ |  |  |  |
| Item | Description/Details | Quantity | Location |
| Item | Description/Details | Quantity | Location |

# Appendix B. Active Records

- Work Orders

- Flushing Reports

- Meter Maintenance Records

- Valve Exercising Records

- Active Inventory

# Appendix C. Emergency Response Plan (ERP)

Do you have a written Emergency Response Plan?

☐ Yes ☐ No

If yes, attach your Emergency Response Plan here