OKLAHOMA CORPORATION COMMISSION

PETROLEUM STORAGE TANK DIVISION

(405) 521-4683   FAX:  (405) 521-4945

SUMMARY OF UST REGULATIONS SPECIFIC TO OKLAHOMA

EFFECTIVE NOVEMBER 1, 2018

Federal regulations require states develop training programs that are specific to their state.  In an effort to meet this requirement the Oklahoma Corporation Commission (OCC) Petroleum Storage Tank Division (PSTD) requires individuals who desire to become a certified operator in Oklahoma who received certification as Class A, B, or C operator in another state, read the following information to be aware of Oklahoma's state specific regulations. The summary addresses regulations where Oklahoma may differ from other states or the federal government. It does not cover all OCC/PSTD requirements for underground storage tanks (USTs). All UST facilities must have Operator Training Certificates available to PSTD.

NOTIFICATIONS

Use of the designated PSTD Scheduling Form is required for the following:

- Installations: PSTD must be given forty-eight (48) hours notice. (OAC 165:25-1-42)

- Repairs: PSTD must be given prior notice. (OAC 165:25-1-54)

- Removals/Closures:  PSTD must be given fourteen (14) days notice. (OAC 165-25-1-42)

- Reschedules: PSTD must be given forty-eight (48) hours notice to reschedule an installation or closure. (OAC 165:25-1-42; OAC 165-25-2-131)

- Tank and Line Tightness Testing, Line Leak Detector and CP Testing: All testing must be scheduled with the PSTD.  Results of testing in which any part of the system does not pass must be reported to the PSTD within twenty-four (24) hours by any person, including the owner, operator, their employees or agents; and separately by the person or company performing the tests. (OAC 165:25-1-48; OAC 165:25-2-53)

- Internal Lining Inspections:  PSTD must be given forty-eight (48) hours notice. (OAC 165:25-2-53.1)

- Compatibility: PSTD must be notified thirty (30) days prior to switching to regulated substances containing greater than ten percent (10%) ethanol or twenty percent (20%) biodiesel. (OAC 165:25-1-53)

LICENSING (OAC 165:25-2-31; 165:25-2-111; 165:25-2-136; 165:25-2-131)

- All installations, closures, removals, and repairs of storage tank systems must be performed by individuals licensed by the PSTD for work within the state of Oklahoma.

OPERATOR TRAINING (OAC 165:25-1-53; 165:25-1-120; 165:25-1-122; 165:25-1-124;

165:25-1-126)

- Oklahoma has an online operator training program that is provided free to Oklahoma storage tank owners and operators.

- All facilities must have Oklahoma Operator Training Certificates available to the PSTD.

- Refresher training is required every three (3) years. PSTD Fuel Specialists may require refresher training earlier if upon inspection a facility is non-compliant.

- All Oklahoma facilities must have a certified Class A, B, and C operators by July 1, 2011.

SECONDARY CONTAINMENT AND INTERSTITIAL MONITORING (OAC 165:25-2-33; 165-25-3-6.21)

- In order to comply with EPA requirements all newly installed tanks and/or product lines must be secondarily contained. The interstitial space of tanks and product lines installed after July 1, 2008, must be monitored for release detection purposes.

OVERFILL (OAC 165:25-2-39)

- A drop tube with overfill device is required on all storage tank systems installed after July 1, 2001.  Tanks installed before July 1, 2001, must be upgraded to meet these standards before July 1, 2002, unless documentation can be provided at the time of inspection for compliance that proves the storage tank system is equipped with an operational ball float overfill device.  Ball float devices cannot be repaired and must be replaced if they become defective.  A ball float vent valve cannot be used on tanks with a suction type system.

- Staff may require a ball float functionality test.  Drop tube flapper overfill devices must be inspected for proper operation every three (3) years and certified as functional.

- Ball float valves that are inoperable cannot be repaired or replaced with another ball float valve.

RELEASE DETECTION (OAC 165:25-3-1; 165:25-3-6.23; 165:25-3-6.24; 165:25-3-6.26; 165:25-3-6.28)

- All tanks must be monitored for releases and have a passing result at least once every thirty (30) days.

- Vapor monitoring and groundwater monitoring rules provide specifics for well installation, number of wells required, instruments for vapor monitoring, reportable levels for vapor monitoring, and site assessments.  An individual must be licensed by PSTD as a Vapor and/or Groundwater Monitoring Well Technician to read vapor or groundwater wells for release detection purposes.

- Automatic Tank Gauges (ATGs) that cannot detect a 0.1 gallon per hour (gph) leak rate every thirty (30) days are required to have thirty (30) day inventory reconciliation done in conjunction with a 0.2 gph or continuous statistical leak detection (CSLD) test.

- Statistical Inventory Reconciliation (SIR) is only accepted as a release detection method for tanks.

CORROSION PROTECTION/INTERNAL LINING (OAC 165:25-2-53.1)

- A previously lined steel tank that fails precision tightness testing may not be repaired and must be removed.

- Tank lining may not be used as a method of repair for a leaking tank.

- UST owners must submit to the PSTD a copy of the certificate of performance (Interior Lining Inspection Form) completed by the inspection provider attesting that the UST meets the performance requirements for both the UST and the lining material.

- Any UST failing the meet the specified performance requirements cannot be relined.  Minor imperfections (see PSTD guidance, "Internal Tank Lining Requirements" for additional information) may be repaired and the tank must be upgraded with a cathodic protection system within six (6) months of the lining repair, or it must be removed.  Suitability of the tanks for upgrade by adding cathodic protection must be determined prior to application.

TANK CLOSURE AND RETURN TO SERVICE (OAC 165:25-2-131; 165:25-2-134)

- Tanks and lines must be removed upon closure unless the Commission grants a variance that allows the tanks and/or lines to be closed in place by filling (typically only granted when tank is buried completely or partially under a building).

- Tank tightness, line tightness, and line leak detector tests must be performed by a certified tester prior to returning to service if the system has been out of service for more than twelve (12) months.

RED TAG AUTHORITY (OAC 165:25-1-67)

- EPA requires states to prevent delivery into fuel tanks that do not meet certain guidelines.  PSTD uses a method called "Red Tag Authority" in order to comply with EPA guidelines.  If a facility violates any of the items listed in OAC 165:25-1-67 "Shutdown of operations" an out of order tag may be placed on the dispenser or fuel tank to prevent the further sale or delivery of fuel.

FINANCIAL RESPONSIBILITY (OAC 165:25-1-24; OAC 165:26-1-22; 165:27-3-1; 165:27-3-2; 165-27-7-2; 165:27-7-7)

- Tank owners must meet financial responsibility requirements in accordance with 40 CFR Part 280 Subpart H.  In Oklahoma this means tank owners must be ready and able to pay an Indemnity Fund co-payment amount up to 1% of the total cost of corrective action, paid in $1,000 increments, not to exceed $5,000. Releases discovered prior to June 4, 2004 require the full $5,000 co-payment. The maximum reimbursement amount for corrective actions at petroleum release sites is $2.5 million. Some tank owners are not eligible to receive reimbursement from this fund. Please review the exclusions found in OAC 165:25, OAC 165:26, and OAC 165:27 for a complete list.

- Eligibility for Indemnity Fund applicants is based on three (3) critical factors, an eligible tank, an eligible substance and an eligible person. Responsible party applicants must be in substantial compliance with all OCC regulations for the twelve (12) thirty (30) day periods prior to the release report date. Fines are assessed for instances of non-compliance.