# OKLAHOMA CORPORATION COMMISSION – PETROLEUM STORAGE TANK DIVISION P. O. Box 52000, Oklahoma City, OK 73152-2000 (405) 521-4683

# PRESSURIZED PRODUCT LINE LEAK DETECTOR TESTS

## DATE TEST COMPLETED			FACILITY NAME						FACILITY ID NUMBER

□ MECHANICAL   	            □ ELECTRONIC

FACILITY ADDRESS			CITY/ZIP					LINE LEAK DETECTOR TYPE CHECK ()

# ELECTRONIC LINE LEAK DETECTION

IF ELECTRONIC LINE LEAK DETECTORS, ARE THEY CONNECTED TO AUTOMATIC TANK GAUGE?    □  YES	   □  NO

_______

MAKE / MODEL OF AUTOMATIC TANK GAUGE			MAKE / MODEL OF ELECTRONIC LINE LEAK DETECTOR(S)

Electronic line leak detectors must be capable of and must perform a 0.2 gallon-per-hour leak test at least once every 30 days (this function is programmed into the electronic control device); and it must be capable of and must perform a 0.1 gallon-per-hour leak test once each year (this function may be programmed or may require manual start by the operator). Operator must provide written proof of these tests (30-day & yearly) being completed successfully. Record below the date each month of the 0.2 gph tests and the date of the annual 0.1 gph test.

ENTER DATE OF EACH 0.2 GPH LINE TEST BY ELECTRONIC LINE LEAK DETECTOR (ATTACH ATG PRINTOUTS):

## Product: ______________Jan. ____  Feb. ____  Mar. ____  Apr. ____  May ____  June ____  July ____  Aug. ____  Sept. ____  Oct. ____  Nov. ____  Dec. ____

Product: ______________Jan. ____  Feb. ____  Mar. ____  Apr. ____  May ____  June ____  July ____  Aug. ____  Sept. ____  Oct. ____  Nov. ____  Dec. ____

## Product: ______________Jan. ____  Feb. ____  Mar. ____  Apr. ____  May ____  June ____  July ____  Aug. ____  Sept. ____  Oct. ____  Nov. ____  Dec. ____

Product: ______________Jan. ____  Feb. ____  Mar. ____  Apr. ____  May ____  June ____  July ____  Aug. ____  Sept. ____  Oct. ____  Nov. ____  Dec. ____

ANNUAL 0.1 GPH LINE TEST BY ELECTRONIC LINE LEAK DETECTOR (ATTACH ATG PRINTOUTS):

Product: _______________  Date Passed 0.1 Annual Test _________________    Product: _______________  Date Passed 0.1 Annual Test _________________

Product: _______________  Date Passed 0.1 Annual Test _________________    Product: _______________  Date Passed 0.1 Annual Test _________________

# FUNCTION TEST OF ELECTRONIC OR MECHANICAL LINE LEAK DETECTION

ANNUAL MECHANICAL LINE LEAK DETECTOR TEST PERFORMED BY:  (Name / Company)___________________________________________

Test Method (must detect 3 gph @ 10 psi leak):________________________________

ANNUAL ELECTRONIC LINE LEAK DETECTOR TEST PERFORMED BY:   (Name / Company)___________________________________________

Test Method (must detect 3 gph @ 10 psi leak)_________________________________

ELLD Function Tests-complete next section below and attach printouts that document system shut down or alarmed when tested.

Technician Telephone No.:  _____________________________    		Technician Signature:_____________________________________

| ### (1) ### Product | (2) Type & Serial Number | (3) Opening Time | (4) Operating Pressure (PSI) | (5) Metering Pressure (PSI) | (6) Measured Leak Rate – Specify Gal/Hr | (7) Pass/Fail |
| --- | --- | --- | --- | --- | --- | --- |
| If Diesel, must use Diesel leak detector | If not recording serial #, explain why. | Seconds required to open to full pressure. | Full pump pressure. | Detector in leak mode, nozzle closed. | Quantity & Duration of created leak. | Includes proper installation per manufacturer |
| With LLD in Leak Mode, open nozzle. Flow should be 1½ to 3 gallons/hour. Close nozzle & observe pressure, while continuing to create leak; pressure should return to rate in column 5. If full line pressure (column 4) is achieved with nozzle closed & created leak in progress, FAIL. |  |  |  |  |  |  |
| (1) |  |  |  |  |  |  |
| (2) |  |  |  |  |  |  |
| (3) |  |  |  |  |  |  |
| (4) |  |  |  |  |  |  |
| (5) |  |  |  |  |  |  |
| (6) |  |  |  |  |  |  |

Revised March 2022                                           TEST WILL BE RETURNED IF FORM IS INCOMPLETE